## Technical Specifications
ANNEXURE 1 TECHNICAL DATA SHEET DUAL FIRED BOILER (NG/OIL) DOC NO KAPL/BDP/CG/3251
KARNATAKA ANTIBIOTICS PHARMACEUTICALS PVT LTD |  | 7ACA PROJECT AT UJJAIN (M.P) | DOSHI CONSULTANT PVT LTD
Sr No | Specification Parameters | Design DCPL/KAPL | Vendor to Fill
A | TECHNICAL DETAILS - | -
A.1 | Basic Specifications & Considerations | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
A.1.1 | Boiler Type | Packaged Smoke Tube type
A.1.2 | Boiler Capacity -
A.1.2.1 | Boiler Capacity 12 TPH F&A 100 Deg C with pressure 10.54 kg/cm2g | 12 TPH F&A 100 Deg C at 10.54 Kg/cm2 (Vendor to Specify Gross & Net Steam Generation at different Load Conditions)
A.1.2.2 | Boiler net steam generation at Boiler W.P. (should be minimum 10 kg/cm2g) & feed water temp : 40 Deg C at the inlet of economizer | (Vendor to Specify Net Steam Generation with NG fuel)
A.1.2.3 | Quantity (Nos.) | 3
A.2 | Boiler Parameters -
A.2.1 | Working Pressure | 10.54 kg/cm2 -Vendor to confirm
A.2.2 | Fuel Parameters | Natural gas NCV - 8500 kcal/sm3 @1-2.5 bar. HSD NCV - 9650 Kcal/Kg (Combustion System should be designed, suitable for both fuels)
A.2.3 | Input Water to the Boiler | Soft Water
A.2.4 | Thermal Efficiency on NCV basis as per BS 845 Part 1 Indirect method | Client to confirm
A.2.5 | Dryness Fraction | 98% minimum
A.2.6 | Boiler response time | Faster to meet the process requirement during high load variation
A.2.7 | Boiler start up time | From Cold start up
A.2.8 | Free board distance
A.2.9 | Location of the Boiler & Space availability | At Boiler House - Attached Layout Drawing (Space Available = to be checked and verified)
A.2.10 | Steam Application Details | For Miscellaneous and Process Heating Applications across the Plant
A.2.11 | Site Condition & Metrological Data | As per Ujjain - Madhya Pradesh
A.2.12 | Type of mounting | Boiler should be skid mounted preferably
A.2.13 | Design Code | As per the IBR 1950 with latest amendments
A.2.14 | Boiler number of Passes | As per Supplier's Design - To be indicated
A.2.15 | Feed Water | Soft Water at 30 deg C
A.2.16 | Design Pressure at Main Stop Valve outlet | Vendor to specify
A.2.17 | Design Steam Type / Temperature | Saturated
A.2.18 | Boiler Hydro Test Pressure | As per Supplier's Design - To be indicated
A.2.19 | Safety Valve Qty & Set Pressure | 2 Nos Safety Valves, Setting as per Supplier & IBR Guidelines
A.2.20 | Steam to Fuel Ratio | As per Supplier's Design - To be indicated
A.2.21 | Heat Output | As per Supplier's Design - To be indicated
A.2.22 | Furnace volume in m3 | As per Supplier's Design - To be indicated
A.2.23 | Volumetric Heat Release Rate | As per Supplier's Design - To be indicated
A.2.24 | Heating Surface Area of boiler in Sqmtrs | As per Supplier's Design - To be indicated
A.2.25 | Heating Surface Area of Economiser | As per Supplier's Design - To be indicated
A.2.26 | Flue gas temp at the outlet of Boiler | As per Supplier's Design - To be indicated
A.2.27 | Flue gas temp at the outlet of Economiser | As per Supplier's Design - To be indicated
A.2.28 | Condensate Reused - | Yes the same shall be recovered from plant
A.2.29 | Boiler Overall Dimensions | As per Supplier's Design - To be indicated
A.2.30 | Boiler Shell OD / Casing Dimension | As per Supplier's Design - To be indicated
A.2.31 | Boiler Shell / Casing Length | As per Supplier's Design - To be indicated
A.2.32 | Furnace Type | As per Supplier's Design - To be indicated
A.2.33 | Furnace Length | As per Supplier's Design - To be indicated
A.2.34 | Furnace thickness | As per Supplier's Design - To be indicated
A.2.35 | Shell Thickness | As per Supplier's Design - To be indicated
A.2.36 | Shell Material | As per Supplier's Design - To be indicated
A.2.37 | Tubes Material | As per Supplier's Design - To be indicated
A.2.38 | Tubes OD in mm | As per Supplier's Design - To be indicated
A.2.39 | Tube Thickness in mm | As per Supplier's Design - To be indicated
A.2.40 | Steam Volume in m3 | As per Supplier's Design - To be indicated
A.2.41 | Gross Weight of Boiler | As per Supplier's Design - To be indicated
A.2.42 | Insulation & Cladding for Boiler | 2 Levels of insulation and cladding or The insulation thickness shall be 100 mm LRB matress with density of 100 Kg/m3 and 24 gauge stucco aluminium cladding
A.2.43 | Boiler surface temperature | Ambient + 10 Deg C max
A.2.44 | Refractory | Hysil block and as per OEM std
A.2.45 | Duty | Continuous / Intermittent
A.2.46 | Mountings and accessories for each boiler
A.2.46.1 | Main Steam stop valve | 1 No.
A.2.46.2 | Safety valves | 2 No.
A.2.46.3 | Pressure gauge 10" Dial size | 1 No
A.2.46.4 | Isolation valve for pressure gauge | 1 No
A.2.46.5 | Feed check valve | 1 No.
A.2.46.6 | Feed NRV (Disc Check valve) | 1 No.
A.2.46.7 | Auxilliary vent valve | 1 No.
A.2.46.8 | Instrument header valve | 1 No.
A.2.46.9 | Blowdown valve | 1 No.
A.2.46.10 | Isolation valves for Water level controller | 2 No.
A.2.46.11 | Water level controller | 1 No.
A.2.46.12 | Water level controller drain | 1 No.
A.2.46.13 | Level gauges | 2 No.
A.2.46.14 | Inspector test gauge cock | 1 No.
A.2.46.15 | Isolation valves for Inspector Test Gauge Cock | 1 No.
A.2.46.16 | Drain pipes for water level controller and Level gauges | SS Tubes
A.2.46.17 | Isolation valves for level transmitter | 1 No.
A.2.46.18 | Level transmitter | 1 No.
A.3 | Burner details - | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
A.3.1 | Burner Type | Pressure jet Dual Block
A.3.2 | Burner Specifications | Standard - Compatible with both HSD & Natural Gas
A.3.3 | Burner Make | FM / OILON/Eq
A.3.4 | Regulation | ECR - Stepless Modulation
A.3.5 | Modulation | Stepless Modulation ECR
A.3.6 | Ignition method | High Voltage Spark
A.3.7 | Burner Turndown Ratio | As Per Supplier design - Turndown Ratio should be 1:4 on HSD and 1: 5 on NG
A.4 | FD fan details - | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
A.4.1 | Flow Capacity = | As per Supplier's Design - To be indicated
A.4.2 | Pressure = | As per Supplier's Design - To be indicated
A.4.3 | Pressure drop across the system = | As per Supplier's Design - To be indicated
A.4.4 | Motor Power Rating = | As per Supplier's Design - To be indicated
A.4.5 | Motor Type = | Squirrel cage induction type, TEFC, IP55, Class F Insulation. high efficiency motor.
A.4.6 | Ducting = | Between Burner and Blower
A.4.7 | Ducting thickness in mm= | Vendor to specify
A.5 | Feed Water Pump details - | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
A.5.1 | Type | Centrifugal multistage
A.5.2 | Quantity (Nos.) | 2 (1 W + 1 S)
A.5.3 | Make | Grundfos / Wilo/Xylem / Eq
A.5.4 | Model | Vendor to specify
A.5.5 | Capacity m3/hr | Vendor to specify
A.5.6 | Head (MLC) suitable | Vendor to specify
A.5.7 | MOC (body / Internals) | Vendor to specify
A.5.8 | Type of sealing | Vendor to specify
A.5.9 | Pump Speed (RPM) | Vendor to specify
A.5.10 | Power Consumption (kw) | Vendor to specify
A.5.11 | Motor type | Vendor to specify
A.6 | Heat Recovery Unit - Design Parameters | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
A.6.1 | Economiser type | Non-Integral Separately-Mounted Economizer (Pressurized type) - To be provided with Bypass Arrgt.
A.6.2 | Design code | As per the IBR 1950 with latest amendments
A.6.3 | Bypass arrangement of Economizer | Yes to be provided with Motorized dampers - 3 No's with feedback to PLC
A.6.4 | Economiser Tubes Material | As Per Supplier design
A.6.5 | Economiser Tubes OD | As per Supplier's Design - To be indicated in Offer
A.6.6 | Economiser Tube Thickness | As per Supplier's Design - To be indicated in Offer
A.6.7 | Empty Weight of Economiser | As per Supplier's Design - To be indicated in Offer
A.6.8 | Flooded Weight of Economiser | As per Supplier's Design - To be indicated in Offer
A.7.3 | Flue Gas Data @ Natural Gas System - | Battery limit
A.7.3.1 | Flue Gas Flow (in m3/hr) @ 100% load = | As per Supplier's Design - To be indicated
A.7.3.2 | Flue Gas Temperature (deg C) = | As per Supplier's Design - To be indicated
A.7.4 | Flue Gas Data @ HSD System - | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
A.7.4.1 | Flue Gas Flow (in m3/hr) @ 100% load = | As per Supplier's Design - To be indicated in Offer
A.7.4.2 | Fuel Gas Temperature (deg C) = | As per Supplier's Design - To be indicated in Offer
A.8 | Instrument Air at Inlet of Respective Instruments - | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
A.8.1 | Quality = | To be Specified by Supplier
A.8.2 | Temperature (deg C) = | To be Specified by Supplier
A.8.3 | Pressure (kg/cm2) = | To be Specified by Supplier
A.9 | Electrical Supply at Control Panel Incomer - | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
A.9.1 | Type | 3-Phase AC (4-Wire with Neutral)
A.9.2 | Supply Voltage (V AC) = | 415
A.9.3 | Control Voltage (V AC) = | 230
A.9.4 | Frequency (Hz) = | 50
A.10 | Gas Train | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
A.10.1 | Gas filter | Vendor to specify
A.10.2 | Gas Pressure Regulating valve | Vendor to specify
A.10.3 | Slam shut off valve | Vendor to specify
A.10.4 | Inlet and Outlet Pressure gauges | Vendor to specify
A.10.5 | Inlet isolation valve | Vendor to specify
A.10.6 | Safety valve | Vendor to specify
A.10.7 | Inlet gas pressure | Vendor to specify
B.1 | Ring Main System | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
B.1.1 | Gear Oil Pump/ screw pump with Motor | 2 Nos (1W + 1S)
B.1.2 | Capacity | Vendor to specify
B.1.3 | Make of pump | Entees
B.1.4 | Working Pressure | Vendor to confirm
B.1.5 | Motor rating | Vendor to specify
B.1.6 | Motor type | Squirrel cage induction type, TEFC, IP55, Class F Insulation. high efficiency motor IE 3
B.1.7 | Duplex Filter | Yes to be provided
B.1.8 | Recirculation Header | Vendor to specify
B.1.9 | Pressure gauges | Vendor to specify
B.1.10 | Piping & Valves mounted on Skid | Vendor to specify
C.1 | Three Element Control System | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
C.1.1 | ARCA Control Valve | Vendor to specify
C.1.2 | Level Transmitter | Vendor to specify
C.1.3 | Steam Flow Meter Vortex Type – IBR | Vendor to specify
C.1.4 | Water Flow Meter Vortex Type - IBR | Vendor to specify
C.1.5 | Programming through PLC | Vendor to specify
D.1 | Electrical Details / Considerations | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
D.1.1 | Power Supply Data -
D.1.1.1 | LT AC | 415V +-10%,
D.1.1.2 | No of Phases | 3P, 3 Wire with 1 neutral
D.1.1.3 | Neutral | Earthed
D.1.1.4 | Frequency | 50Hz +-5%
D.1.1.5 | Motor Control Centre (415V Motors)
D.1.6.6 | Incomer | MCCB <~630;ACB>630;LSIG;ICw>=50kA for 1 Sec;Latest Release
D.1.6.7 | Main Bus Bar | Electrolytic Grade with Current Density 0.60A per sq mm
D.1.6.8 | Metering | MFM EM6400 NG for Incomer
D.1.6.9 | IMCC Panel | 2mm CRCA,Free standing; Double front; Compartmentalized Suitable for Ambient 50°C;Cable entry bottom / top
D.1.6.10 | Variable Speed Motors
D.1.6.11 | Type | VFD duty;415V ;3P;VPI Coated;Ambient 50°C;IP55
D.1.6.12 | Insulation | F Class Insulation Temp rise upto Class B (with VPI Coating)
D.1.6.13 | Rating | 150% overload for 60sec in every 300sec
D.1.6.14 | Cooling method | Air cooling
D.1.6.15 | Fixed Speed Motors
D.1.6.16 | Type | S1 duty;415V ;3P;Ambient 50°C;IP55
D.1.6.17 | Insulation | F Class Insulation Temp rise upto Class B (with VPI Coating)
D.1.6.18 | Efficiency Class | IE3
D.1.6.19 | Basic Automation
D.1.6.20 | PLC CPU | S7-300 or equivalent ,Utilisation should not be more than 80% (other make to be discussed if applicable )
D.1.6.21 | DI/DO | 32bits;24Vdc with 15% spares points
D.1.6.22 | AI/AO | Universal type +-10V;0-20mA;4-20mA & 15% spares points
D.1.6.23 | Communication Modules | As per requirements
D.1.6.24 | Burner Firing logic | To be as per standard
D.1.6.25 | Communication
D.1.6.26 | PLC -HMI | Ethernet or equivalent - Vendor to confirm.
D.1.6.27 | Special Cables | As per requirements
D.1.6.28 | Level 2 communication | Data Read /Write for level 2 provision to be made
D.1.6.29 | PLC Panel
D.1.6.30 | Construction | 2mm CRCA,Free standing, Powder Coated
D.1.6.31 | Operator Panel | 10" Operator key & Touch Panel
D.1.6.32 | Workstation grade Industrial PC's; Intel I7 processor; 24" LED monitor ;8GB RAM; 1TB storage;2 LAN Ports | As per Supplier's Design
D.1.6.33 | SCADA PC | Work Station Grade Industrial PC with latest OS & Development software licenses for PLC & HMI both
D.1.6.34 | Cables -
D.1.6.34.1 | Communication Cables | As per Requirement
D.1.6.34.2 | Special cables | As per Requirement
E.1 | Documentation -
E.1.1 | Drawings | Two set hard copy as well soft copy to be provided
E.1.2 | Manuals | Manual for all instruments to be provided
E.1.3 | Software backup | To be provided in pen drives min 2 set
E.1.4 | Boiler Control Philosophy | Three-Element Drum Level Control System
F.1 | Chemical Dosing System | LP Dosing with Auto pH correction
G1 | Balance of Plant | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
G1.1 | Feed water tank 20 Kl - 2nos | Vendor to confirm
G1.2 | Type | Atmospheric
G1.3 | Design Pressure | Atmospheric
G1.4 | Material of construction | IS 2062 /Eq
G1.5 | Accessories | 1) Temperature control system. 2) Level control system. 3) Steam heating system. 4) Deaerator head with make up inlet, condensate and flash recovery nozzles and airvent and vacuum breaker
G1.6 | Operation | All the controls to be vested in PLC and Scada
G1.7 | Control valves / Piston actuated valves | The same shall be pneumatically operated along with inlet, outlet and bypass valves to be provided
G1.8 | Piping and ducting as per agreed battery limits | To be mentioned
G1.9 | Softener Plant | CLIENT SUPPLY
G1.10 | Engineering of Steam piping from Boilers and accessories with interconnecting piping as per given KAPL Layout | All piping to be designed for minimum possible steam side pressure drop. Engineering of piping from process outlet till trench / outlet/inlet ; • Line sizing • Routing • Primary supports • Bill of material of piping / Insulation
H | QUALITY ASSURANCE DETAILS -
H.1 | Steam Generation Data vs Fuel Consumption | <TO BE INDICATED BY SUPPLIER>
H.1.1 | 100% Boiler Load at 10.54 kg/cm2 Steam Pressure | Fuel Consumption @Supplier's Design to be indicated
H.1.2 | 75% Boiler Load at 10.54 kg/cm2 Steam Pressure | Fuel Consumption @Supplier's Design to be indicated
H.1.3 | 50% Boiler Load at 10.54 kg/cm2 Steam Pressure | Fuel Consumption @Supplier's Design to be indicated
H.2 | Guarantee Parameters (during Full Load Run) | <TO BE INDICATED BY SUPPLIER>
H.2.1 | Boiler efficiency with heat recovery system in line | As Settled & Mutually Agreed with the Supplier
H.2.2 | Boiler efficiency with heat recovery system in by pass mode | As Settled & Mutually Agreed with the Supplier
H.2.3 | Temperature of the Flue gas after Economizer | As Settled & Mutually Agreed with the Supplier
H.2.4 | Oxygen Percentage in Flue gas | As Settled & Mutually Agreed with the Supplier - Provision & Automation Feedback for O2 Analyzer to be Considered.
H.3 | Quality Assurance Conditions | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
H.3.1 | Measurement Procedure for Guarantee Items | As per Mutual Agreement
H.3.2 | Submission of Quality Assurance Procedure (QAP) - (Alongwith the GA Drg) For KAPL Approvals before Boiler Manufacturing ) | Supplier to Furnish QAP to be followed under Boiler Manufacturing
H.3.3 | Performance Test | To be carried out at KAPL Site during Commissioning Stage
H.4 | Make List for Boiler Components | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
H.4.1 | Mechanical Items > | Make Options
H.4.1.1 | Feed water Pump | Wilo / Grundfoss /Xylem (Vertical Type, with Mechanical Seal)
H.4.1.2 | Burner | FM/ OILON/Eq
H.4.1.3 | Gas train | Kromschroder / Dungs / VANAZ/Eq
H.4.1.4 | Blower Burner FD Fan & ID Fan | Laxmi Engineering /Eq
H.4.1.5 | Main Steam Stop Valve & Mobrey isolation Valve | Forbes Marshall/L&T Eq
H.4.1.6 | Gate / Globve Valve | Forbes Marshall / L & T /Eq
H.4.1.7 | Non Return Valve | Forbes Marshall / KSB / L & T
H.4.1.8 | Safety Valve | Forbes Marshall / Fainger Lager / Darling Muesco /Eq
H.4.1.9 | Manual Blow Down Valve | Bonetti / Levcon / Pennant / Inditech system /Eq
H.4.1.10 | Ball Valves | Forbes Marshall / KSB / L & T
H.4.1.11 | Pressure Gauges | Forbes Marshall / H Guru / GIC / Wika
H.4.1.12 | Orifice Plate | Reputed
H.4.1.13 | Level Gauge | Forbes Marshall / Techtrol/Eq
H.4.1.14 | Fusible Plug | Leader / Neta/Eq
H.5 | Electrical Items > | Make Options
H.5.1 | Energy Efficient Motors (IE 3) | CG / Siemens / ABB
H.5.2 | Level Transmitter | Emerson / Rosemount / Siemens / E&H
H.5.3 | Water level controller | Malhotra / Techtrol
H.5.4 | Pressure switch | Danfoss /Eq
H.5.5 | Electrical Control Panel | OEM standard
H.5.6 | Cables | Polycab / Universal / RR
H.5.7 | Control Valves / Piston actuated valves | Forbes Marshall / MIL / Emerson / Fisher
H.5.8 | DCV | Forbes Marshall / L&T
H.5.9 | Switchgear | Siemens /L&T/Eq
H.5.10 | Pressure Transmitter | Danfoss/Honey well/Eq
H.5.11 | Level guage cum switches | Techtrol / Chemtrol/Eq
H.5.12 | Solenoid Valves | Rotex / Schrader/Eq
H.5.13 | Temperature Sensors / Transmitters | Radix/Danfoss/Eq
H.5.14 | Cable Lugs | Dowell's / Comet / Braco/Eq
H.5.15 | Cable Gland | Dowell's / Comet / Braco/Eq
H.5.16 | Push Buttons & Its element | Teknic / Siemens/Eq
H.5.17 | MCB | Siemens /L& T/ Eq
H.5.18 | Terminal Box | Elemex / Connectwell/Eq
H.5.19 | Selector Switch | Teknic / Siemens/Eq
H.5.20 | O2 Sensor | Zirconia based insitu type/Eq
H.5.21 | Energy Meters | EM6436 (Schneider) with Rs485 communication
H.5.22 | Steam/Gas flow meters | Smart with Local Display
I.2 | List of Document Submissions | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
I.2.1 | Documents Required During Execution Stage >
I.2.1.1 | Typical GA Drawing & P&I Drawing of the Boilers (Duly-Agreed-&-Signed-with-Seal) | As per Supplier's Design - To be Furnished with Offer
I.2.1.2 | Quality Assurance Plans (Duly-Agreed-&-Signed-with-Seal) | As per Supplier's Recommendations
I.2.1.3 | List of Makes for Bought-out Spares (Mech+Elec) (Duly-Agreed-&-Signed-with-Seal) | As per Supplier's Submission
I.2.1.4 | Project Execution Schedule / Barchart (indicating Period Milestones & Duration – e.g., for Kick-off Meeting, Drawing Submission, Material Readiness, Inspection Calls, Material Dispatch, Erection & Commissioning, Final Acceptance Test etc) (Duly-Agreed-&-Signed-with-Seal) | As per Supplier's Submission @Delivery Target by KAPL
I.4 | Delivery Schedule & Guarantee Clause | <TO BE CONFIRMED / INDICATED BY SUPPLIER>
I.4.1 | Delivery Period for Supply | Target = 5 Months
I.4.2 | Duration of Erection & Commissioning | Target = 2 Month
I.4.3 | Guarantee / Warranty | 18 Months from the date of supply or 12 months from the date of commissioning whichever is later
Note: | Eq = Equivalent make shall have prior approval from DCPL & KAPL.