## TECHNICAL SHEET_700TR
ANNEXURE 1 TECHNICAL DATA SHEET FOR WATER COOLED CENTRIFUGAL CHILLER DOC NO KAPL/BDP/CG/3252
Karnataka Antibiotics and Pharmaceutical Ltd |  | 7ACA PROJECT AT UJJAIN | DOSHI CONSULTANTS PVT. LTD.
SR.NO. | Descriptiuon | Specification | VENDOR TO PROVIDE DEATIL
1 | Type | Centrifugal chiller
2 | Components | VFD Driven Centrifugal Chiller
Refrigerent Piping /Condenser/ Instrumentation
3 | No. of Units | 4
4 | Refrigeration Capacity, TR at duty point | 700
5 | Refrigerant | R134a /R514 /1234 ze/Equivalent
6 | a) Refrigerant Flow Rate, m³/hr | Vendor to specify
| b) Initial Charge, Kg | Vendor to specify
7 | Refrigerant Latent Heat, KCal/Kg. | Vendor to specify
8 | Type | Water cooled
9 | Certification | AHRI/ARI 550
10 | IKW/TR | Less than 0.60 - Vendor to confirm
11 | COP of chiller | 6.0 and above - Vendor to confirm
12 | NPLV AHRI | Vendor to specify
13 | Full load sound pressure at 1 mtr level | 80 DB vendor to confirm
14 | Chiller heat rejected capacity to atmosphere | Vendor to specify
Chiller Design Data
15 | Evaporator Water Temperature at Inlet, ºC | 12
16 | Evaporator Water Temperature at Outlet, ºC | 7
17 | Condenser Water Temperature at Inlet, ºC | 32
18 | Condenser Water Temperature at Outlet, ºC | 36
19 | Properties of Water at Mean Temperature
a) | Specific Heat, KCal/Kg./ ºC | 1
b) | Specific Gravity | 1
c) | Viscosity (Cp) | 1
d) | Thermal Conductivity KCal/Hr. Mtr. ºC | Vendor to specify.
20 | COMPRESSOR
a) | Model / Type | Centrifugal Vendor to specify Make & Model.
b) | No. of Stages | Vendor to specify.
c) | RPM | Vendor to specify.
Vendor to specify.
d) | Compression Ratio | Vendor to specify.
e) | Capacity, KCal/Hr. | Vendor to specify.
f) | SST, ºC | Vendor to specify.
g) | DST, ºC | Vendor to specify.
h) | Compressor Details | Vendor to specify.
| Compressor Size | Vendor to specify.
| Impeller Size | Vendor to specify.
| Orfice size | Vendor to specify.
| Motor size | Vendor to specify.
i) | Motor Details | Vendor to specify.
1) | Make | Vendor to specify
2) | Type | Squirrel Cage, Air /gas Cooled. Vendor to confirm.
Inverted Duty, VFD Driven, IE-3, 2 Pole, TEFC, IP54, Flange Mounted.
3) | H.P / RPM | 2980 - Vendor to confirm.
4) | Supply | 415 ±10% V, 50 ±5%Hz, 3 phase, Induction Motor
5) | Rating | Continuous
6) | Power Transmission | Direct / Other. Vendor to specify.
7) | Motor LRA | Vendor to specify.
8) | Compressor Motor RLA | Vendor to specify.
9) | Primary RLA(Incoming line) | Vendor to specify.
10) | Minimum Circuit amp | Vendor to specify.
11) | Maximum Over current protection | Vendor to specify.
12) | Insulation Class | Class F with TR to Class B. Vendor to confirm.
13) | Efficiency Class | IE - 3
j) | Capacity Control Step-wise / Stepless | Vendor to specify.
k) | Lubrication System | Vendor to specify.
1 | Type | Vendor to specify.
2 | Lubricant | Vendor to specify.
3 | Lubricant Charge Lts | Vendor to specify.
21 | CONDENSOR
a) | Type | Shell & Tube
b) | Model | Vendor to specify.
c) | Area, M² | Vendor to specify.
d) | Condenser bundle size/ No. of Tubes | Vendor to specify.
e) | Tube Size | Vendor to specify.
f) | Condenser shell size | Vendor to specify.
g) | Condenser tube type | Vendor to specify.
h) | Condenser tube type | Vendor to specify.
i) | Condenser tube thickness | Vendor to specify.
j) | No. of Passes | Vendor to specify.
k) | Cooling Water Flow Rate, M³./Hr. | Vendor to specify.
l) | Cooling Water Flow Rate, M³./Hr.(Max) | Vendor to specify.
m) | Cooling Water Flow Rate, M³./Hr.(Min) | Vendor to specify.
n) | Cooling Water
| 1) Inlet Temperature, ºC | 32
| 2) Outlet Temperature, ºC | Vendor to specify. 36ºC (Maximum)
0) | Pressure Drop mtr maximum | 2.5 - Vendor to confirm.
| Pressure Drop mm at maximum flow | Vendor to specify.
| Pressure Drop mmcat minimum condenser flow | Vendor to specify.
p) | Fouling Factor, Hr. Sq.Mtr. ºC/KCal. As per ARI 550 | 0.0002 - Vendor to confirm.
q) | Design Temperature, ºC | 50
r) | Standard | TEMA
s) | Flow condenser/refrigeratiioncapacity)
t) | Marine water box | Required - vendor to confirm
u) | Tube side fluid | Water - vendor to confirm
22 | CHILLER / EVAPORATOR | Flooded/DX
a) | Type | Shell & Tube
b) | Model | Vendor to specify.
c) | Area, Sq. Mtr. | Vendor to specify.
d) | evaporator bundle size/ No. of Tubes | Vendor to specify.
e) | Tube Size | Vendor to specify.
f) | evaporator shell size | Vendor to specify.
g) | evaporator tube type | Vendor to specify.
h) | evaporator tube type | Vendor to specify.
i) | evaporator tube thickness | Vendor to specify.
j) | No. Of Passes | Vendor to specify.
k) | Refrigerant Flow Rate, Kg./Hr. | Vendor to specify.
l) | Refrigerant Temperature | Vendor to specify.
| 1) Inlet Temperature, ºC | Vendor to specify.
| 2) Outlet Temperature, ºC | Vendor to specify.
m) | Water Flow Rate, m³/hr | Vendor to specify.
| Evaporator Water Flow Rate, M³./Hr.(Max) | Vendor to specify.
| Evaporator Water Flow Rate, M³./Hr.(Min) | Vendor to specify.
n) | Pressure Drop, MLC | Vendor to specify.
| Pressure Drop mm at maximum flow | Vendor to specify.
| Pressure Drop mmcat minimum r fow | Vendor to specify.
o) | Fouling Factor, Hr. Sq.Mtr. ºC/KCal. As per ARI 550 | 0.0001. Vendor to confirm.
p) | Flow evaporator/refrigeratiioncapacity)
q) | Marine water box | Required - vendor to confirm
r) | Tube side fluid | Water - vendor to confirm
23 | OIL SEPARATOR
a) | Type | Pressure Vessel
b) | Separation Method | SS 304 Demister/ Other. Vendor to confirm.
c) | Model / Size | Vendor to specify.
d) | Quantity, Nos. | 1
24 | CONTROL PANEL
a) | Type & Make | Microprocessor Based / Vendor to specify. Siemens/eq Make preferred.
b) | Type of HMI | LCD with Key Pad
c) | Mode of Operation | Auto / Manual. Vendor to confirm.
d) | BMS Compatibility | Required. Vendor to specify.
e) | Type of starter | Variable speed vendor to confirm
f) | PC Connectivity for Monitoring the parameters | Required - vendor to confirm
25 | Data Available on Display | Required. Vendor to specify.
1) | Suction Pressure | Vendor to confirm
2) | Discharge Pressure | Vendor to confirm
3) | Chilled Water Inlet Temperature | Vendor to confirm
4) | Chilled Water Outlet Temperature | Vendor to confirm
5) | Condenser Water Inlet Temperature | Vendor to confirm
6) | Condenser Water Outlet Temperature | Vendor to confirm
7) | Liquid Line Refrigerant Temperature | Vendor to confirm
8) | Suction Line Refrigerant Temperature | Vendor to confirm
9) | Saturated Suction Temperature | Vendor to confirm
10) | Suction Super Heat | Vendor to confirm
11) | Saturated Discharge Temperature | Vendor to confirm
12) | Discharge Line Refrigerant Temperature | Vendor to confirm
13) | Discharge Super Heat | Vendor to confirm
14) | Evaporator Approach Temperature | Vendor to confirm
15) | Condenser Approach Temperature | Vendor to confirm
16) | Compressor Motor Current in Amp (only one Phase) | Vendor to confirm
17) | Compressor Motor Current in % RLA | Vendor to confirm
18) | Date & Time | Vendor to confirm
19) | Compressor ON / OFF | Vendor to confirm
20) | Water Flow ON /OFF indication (Condenser) | Vendor to confirm
21) | Water Flow ON /OFF indication (Evaporator) | Vendor to confirm
23) | Oil Feed Pressure | Vendor to confirm
24) | Differential Oil Pressure | Vendor to confirm
25) | Motor Winding Temperature - Healthy or Un-healthy | Vendor to confirm
26) | Voltage Protection Device - Healthy or Un-healthy | Vendor to confirm
27) | EXV Opening % | Vendor to confirm
28) | Voltage | Vendor to confirm
Safeties - Directly sensed by the Controller & acted upon
| 1) Pressure Alarms | Required
a) | High Discharge Pressure | Required
b) | Low Suction Pressure | Required
c) | Low Oil Pressure Differential | Required
d) | Unsafe Oil Pressure | Required
e) | Dirty Filter Pressure | Required
| 2) Temperature Alarms | Required
a) | High Discharge Temperature | Required
b) | High Oil Temperature | Required
c) | Antifreeze Trip | Required
| 3) Current Alarms | Required
a) | Very high current | Trip required
b) | High Current | Required
c) | Low Current | Required
| 4) Pro Active Unload for | Required
a) | High Current | Required
b) | High discharge Pressure | Required
c) | Low Suction Pressure | Required
5) Flow Switch for water flow
| At evaporator inlet/outlet | Required
| At condenser inlet/outlet | Required
26 | Starter Panel with Motor Protection Device | Variable speed vendor to confirm
27 | Control Wiring | For field Instruments to the Control Panel
28 | Performane data
28.1 | IKW/TR AT DESIGN CONDITION AT AHRI CONDENSER RELEIF | Vendor to specify
100%
90%
80%
70%
60%
50%
40%
28.2 | IKW/TR AT DESIGN CONDITION AT constant condenser water condition | Vendor to specify
100%
90%
80%
70%
60%
50%
40%
28.3 | NPLV/IPLV | Vendor to specify
29 | Power Supply
| Starting current | vendor to confirm
| Full load current | vendor to confirm
30 | Overall Dimensions
| Length M | Vendor to Specify
| Width M | Vendor to Specify
| Height M | Vendor to Specify
31 | Clearances for Maintainance
| Sides M | Vendor to Specify
| Front M | Vendor to Specify
| Back M | Vendor to Specify
| Above Equipment M | Vendor to Specify
| Tube Cleaning M | Vendor to Specify
32 | Weight of Equipment
| Bare Unit kg | Vendor to Specify
| Operating Weight kg | Vendor to Specify
ACCESSORIES
1 | Expansion Valve
a) | Type | Electronic Expansion Valve & IGV
b) | Size | To Suit Chiller
c) | Make | Sporlon or Equivalent
d) | Inlet Pressure, Kg./Cm² | To Suit Chiller
e) | Outlet Pressure, Kg./Cm² | To Suit Chiller
f) | Outlet Temperature, ºC | To Suit Chiller
2 | Thermostat | N/A
a) | Type | N/A
b) | Make | N/A
c) | Range | N/A
d) | Quantity | N/A
3 | Flow switch for evaporator and condenser
a) | Type | Mechanical Flow Swicth
b) | Make | Kelong or Equivalent
c) | Range | To suit Chiller
d) | Quantity | 2 Nos per Chiller
4 | Pressure Gauges
a) | Make | N/A , Via Sensor & Transducer
b) | Quantity | N/A , Via Sensor & Transducer
c) | Range | N/A , Via Sensor & Transducer
5 | Pressure Switches
a) | Type | N/A , Via Sensor & Transducer
b) | Make | N/A , Via Sensor & Transducer
c) | Range | N/A , Via Sensor & Transducer
d) | High Pressure | N/A , Via Sensor & Transducer
e) | Low Pressure | N/A , Via Sensor & Transducer
6 | Temparature gauges
a) | Make | N/A , Via Sensor & Transducer
b) | Quantity | N/A , Via Sensor & Transducer
c) | Range | N/A , Via Sensor & Transducer
7 | Temparature Sensors
a) | Make | Trane OEM Make
b) | Quantity | To suit Chiller
8 | Flow Fail Switches for Water
a) | Make | N/A
b) | Quantity
9 | Sight Glass
a) | Make | Vendor to specify
b) | Quantity
10 | Pilot Line Solenoid Valves | Vendor to specify
a) | Make | Vendor to specify
b) | Quantity
11 | Safety Valves | Vendor to specify
a) | Make | Vendor to specify
b) | Quantity | Vendor to specify
12 | Strainers | Vendor to specify
a) | Make | Vendor to specify
b) | Quantity
13 | Non-Return Valve | Vendor to specify
a) | Make | Vendor to specify
b) | Quantity
Material Specification
1 | Condenser
a) | Shell | IS 2062 Gr. A or equivalent
b) | Tubes | Seamless Copper Tubes Plain End
c) | Tube Sheet / Support Plate | IS 2062 Gr. A or equivalent
d) | End Cover | IS 2062 Gr. A or equivalent
e) | Gaskets | Non-Asbestos - CI42 / AF120
f) | Bolts Nuts | SA 193 Gr. B7 / SA 194 Gr. 2H Or IS STD
g) | Bonnet / Bonnet Flange | IS 2002 / SA 516 Gr. 70
2 | Chiller
a) | Shell | IS 2062 Gr. A /Equivalent
b) | Tubes | Inner Grooved Copper Tubes
c) | Flange / End Cover / Tube Sheet | IS 2062 Gr. A or equivalent
d) | Gaskets | Non CAF / CI 42
e) | Economizer | SS 316
3 | Oil Separator
a) | Shell | CI
b) | End Cover | CI
c) | Bolts Nuts | Manufacturer STD
4 | Interconnecting Piping.
a) | Refrigerant Valves | Danfoss / Castle / Sporlane/Equivalent
b) | Fittings | Sa 234 Gr. WPB / SA 105
c) | Bolts Nuts | SA 193 Gr. B7 / SA 194 Gr. 2H or IS Std.
d) | Gaskets | Non Asbestos
e) | Refrigerant Piping | Copper
f) | Water Piping | IS 1239/ BS 3059/Equivalent
5 | All types of Valves including Safety Valves | Cast Steel body with SS 304 Internals
6 | Insulation of Suction piping and the Chiller | EPDM / Nitrile Rubber.
Misc
1 | Power Supply | Vendor to specify
| Starting current | Vendor to specify
| Full load current | Vendor to specify
2 | Overall Dimensions | Vendor to specify
| Length M | Vendor to specify
| Width M | Vendor to specify
| Height M | Vendor to specify
3 | Performance Tests
a) Power Consumption at 50%, 75% and 100% Load.
b) Capacity Control.
c) All safety-control systems
4 | Load trials at rated TR
5 | Provision to be made for interlocking compressor motor with primary pump and cooling water pump.