## CoolingTower
TECHANICAL DATA SHEET - COOLING TOWERS FOR PROCESS CHILLER DOC NO KAPL/BDP/CG/3253
KARNATAKA ANTIBIOTICS AND PHARMACEUTICALS LTD |  | 7ACA PROJECT AT UJJAIN | DOSHI CONSULTANTS PVT. LTD.
S.No | DESCRIPTION | AS PER TENDER | DATA TO BE FILLED BY CONTRACTOR
1 | COOLING TOWER
| Type | Induced Draft/Forced draft
| Make | Vendor to specify
| Model No | Vendor to specify
| Heat rejection capacity per cooling tower Kcal /HR | 3500 Cooling capacity
| No of cooling Tower | 1
| No of cell per cooling tower | 4 vendor to confirm
per cell heat rejection capacity Kcal/HR
| Certification | CTI approved
2 | Operating Parameters
| No of cooling Tower | 1
| No. of Cells | Four per cooling tower
| Flow Rate CMH For CT | 2634
| Flow Rate CMH For each Cell | 658.5
| Water Inlet Temperature | 31⁰C
| Water Outlet Temperature | 35⁰C
| Max Air inlet Temperature | 41⁰C
| Wet Bulb Temperature | 27.39⁰C
| Location | Ujjain
| Air / Water Flow Direction | Cross flow/counter flow
| Cooling tower approach | Vendor to specify
3 | CASING
| Material of Construction | F R P
| Finish In / Out | Gel Coated, UV Stabilised
| Method of Joining | Bolted / Sealed
| Fills | PVC fill type /Splash bar
| Type | Vendor to specify
| Material | Vendor to specify
| PVC Fills spacing | 25 MM Pitch
4 | BASIN
| Material of Construction | Concrete
| Finish In / Out | Concrete
| Water connections Size | Inlet, Outlet, Float, Quick fill, Overflow Drain vendor to specify
| Water Outlet connection size | vendor to specify
| Quick fill size | vendor to specify
| Over flow size | vendor to specify
| Type | Flanged / Grooved
| Basin Sump quantity and size | Vendor to specify
5 | Water Distribution
| Method | Fixed Nozzles or Rotary Sprinklers
| Material of Nozzle | ABS / SS
| Material of Header | FRP / PVC
6 | Drift Eliminators
| Type | Full Cross Section Coverage
| Material | Vacuum formed PVC
| Flow of Air | Vertical Upward
| Make / Type | Munters D - 15Type /Eq
| Framework / Structural | M S HDG
| Joining Method | Bolted, GI Fasteners
7 | Fan
| Fan Motor | Lowest kW Preferred
| Fan motor KW | Vendor to specify
| Fan Dia | Vendor to specify
| Fan speed | Vendor to specify
| No of Fan | Vendor to specify
| Air Volume | Vendor to specify
| No of Blade | Vendor to specify
| Drive | Gear Type
| Gear type | Vendor to specify
| Gear Ratio | Vendor to specify
| Gear MOC | Vendor to specify
| Service factor | Vendor to specify
| Type | TEFC ,IP -55 weather proof IE 3
| Finish | Paint suitable for moist Air Epoxy Coated
| Fans (s) / Cell | vendor to specify
| Type | Axial with Variable flow
| Blade | Airfoil
| Material Blades | FRP / Al. Alloy
| Material Hub | Heavily galvenized M S or Al. Alloy Hubs with SS hardware
| Material Fastener | Epoxy Coated MSHDGI
| Balancing | Dynamically Balanced Blades & Hub Assembly
| Mounting | Flange / Foot
| Shaft Orientation | Downward / Horizontal
| Louver for Inlet | Yes
| Material | FRP / Aluminium / PVC
| Shaft and coupling | SS 304
| Finish | GEL Coated / Power coated
| Water Treatment | Necessary to maintain Water Quality
| Support Structure | GI/MS, HDG
| Accessories | Access Ladder / Counter Flanges Float Valve / Level Switch/Fan deck railing
| Performance Curve | Required for Standard, 20% Lower, 20% Higher, Flow Rates / for WBT from 20 deg.C to 32 deg.C, and 10% Higher & Lower Range
| Fan Cover | Bird Screen required
8 | Performance
| Evaporation loss | Vendor to specify
| Drift loss | Vendor to specify
| Blown down | Vendor to specify
| Makeup water quantity | Vendor to specify
| Testing | In site, as per CTI
| Performance | As per CTI
| Dimension of cooling tower with out sump | Vendor to specify
| Wt of cooling tower empty | Vendor to specify
| Operating Wt of cooling tower | Vendor to specify