## Sheet1
ANNEXURE - III PRICE BID FOR WATER COOLED CENTRIFUGAL CHILLER
KARNATAKA ANTIBIOTICS & PHARMACEUTICALS LTD. |  | DOC NO KAPL/BDP/CG/3252 |  |  |  |  | DOSHI CONSULTANTS PVT. LTD.
Sl. No | Description of Item | Unit | Quantity (Nos.) | Unit Price |  | Amount in Rs |  | Total Amount in Rs
|  |  |  | Supply | Installation | Supply | Installation
1 | PRICE
1.1 | Design , supply ,installation and commissioning of water cooled centrifugal VFD driven chiller in accordance with section VII scope of work and technical specification section VIII and technical data sheet. Machine mounted starter panel with VFD ,water cooled condenser, insulated chiller ,flows witch chiller and condenser ,vibration isolators, integral refrigerant piping and wiring ,BMS interface unit (Modbus/Banat ),grooved coupling for condenser and cooler water inlet and outlet connection, complete charge of refrigerentand oil. Accessories as required and called for, automatic and safety controls mounted in central micro-processor based console panel and all mounted on a steel frame complete as per specifications. | No | 4
1.2 | Motor shall be suitable for 415±10% 50 cycles. 3 phase AC supply and motor cable terminal box shall be suitable to connect Copper Cabling.
1.3 | Refrigerant used shall be Ozone friendly HFC-134a/ R514/ R1234 Zb/ Equivalent as detailed in specifications. Vendor must provide junction box along with each set of unit including cable works from junction box to chiller. First chiller shall be factory tested at design conditions at 100%, 75%, 50% and 25% load as per AHRI standard in presence of KAPL authority and consultant
1.4 | Cost inclusive of for all chillers port charges, port handling charges, other local duties, loading, transportation/insurance unto site, octroi charges and all other taxes and incidentals complete till delivered at site
1.5 | Cost inclusive of Marine box for condenser and chiller
1.6 | Design Parameter
Capacity 700 TR at duty point
Chilled water inlet and out let 12/7⁰C
Condenser water inlet and out let 36/32⁰C
Total
Total Cost in figure
Total Cost in words
1.7 | Packing / forwarding freight and unloading at site
1.8 | Transit insurance
1.9 | GST
Total deliverable cost at KAPL site Ujjain
1.1 | Extra if any
1.11 | Are prices quoted firm till equipment delivery / commissioning at KAPL Ujjain SITE | Y/N
2 | Bid validity date
3 | Guaranteed delivery date on EX KAPL Ujjain site basis
4 | Terms of payment
4.1 | For Indigenous Item for transportation, port charges , clearance charges, unloading, installation and commissioning
15% Advance against advance bank guarantee validity of entire duration of the project and to be extended on the request of KAPL or until the advances are recovered.
60% after Fat and delivery at site
15 % against installation
10% after commissioning and successful handing over to KAPL
All necessary statutory deductions like GST TDS, Income Tax TDS etc. shall be applicable as per Government norms
For Imported item
4.2 | For Imported item
Against Letter of credit
5 | Payment schedule
Refer Clause 21 of special condition of contract
6 | Guarantees
6.1 | For satisfactory workman ship and against defective materials
6.2 | For Satisfactory performance
7 | Bank Guarantee
7.1 | For advance payment
7.2 | For performance
8 | Insurance
| Contractor all risk policies(CAR) | Required
| Erection all risk policies(EAR ) | Required
NOTE : Cost to be put in words and figure
[5 empty] | Signature |  | ___________________________
[5 empty] | Name and designation |  | ___________________________
| COMPANY SEAL | [5 empty] | ___________________________
[5 empty] | Company |  | ___________________________
[5 empty] | Date |  | ___________________________

## Sheet2
Oil Free Two-Stage integral Centrifugal air compressor with high
efficiency water-cooled motor with sleeve-bearing, stainless steel
intercooler & after-cooler for compressed air requirement of
minimum 11700 cfm with no negative tolerance at 3 barg at the
outlet of the check valve (for design ambient condition of 42 deg C
temperature , 18% RH, and 32 deg C of cooling water temperature
)and max compressor pressure 3.5 barg (scope from 1.1 to 1.19)
Model: ZH1250-3.5 without acoustic enclosure
Motor : 1250kW 11 kV with Sleeve bearing IP55 (ABB/ Atlas Copco/
Equivalent)
Motor Cooling type: IC81W Water-Cooled Version