## Annex II A HT trans
ANNEXURE IIA TECHNICAL DATA SHEET FOR HT TRANSFORMER DOC NO KAPL/BDP/SR/1482
KARNATAKA ANTIBIOTICS AND PHARMACEUTICAL LTD |  |  |  | DOSHI CONSULTANT PVT LTD
S.No. | Description | DCPl Specification | Vendor to provide data | Remark
Technical Specific
1 | Manufacturer's name and address
2 | Rated KVA | 2Nos. X 8000 KVA
2 | Standard Applicable | to feed 11kV Air Compressor
3 | Ref. standards | IS 1180
4 | Installation (Indoor / Outdoor) | Outdoor
5 | Vector Group | Dyn11
6 | Frequency | 50 Hz
7 | Voltage Ratio | 33/11 KV
8 | Winding Material | Copper
9 | Winding Connection | Delta/ Star
Primary/Secondary
10 | Insulation | Class A Uniform
11 | Duty Cycle | Continuous
12 | Degree of Protection | IP55
13 | Cooling System | ONAN
14 | Short Circuit Level at 33 KV | 26.3KA fro 1 Sec.
15 | Rated Primary Voltage | 33 KV
16 | Supply Neutral | Solidly Earthed
17 | Highest System Voltage for Primary | 36 KV
18 | Rated Secondary Voltage (at No­load) | 11 Volts
19 | Supply Neutral | Solidly Earthed by (NGR)
20 | Noise Level | 75 dB(A)-1 Meter(Maximum)
21 | X/R Ratio
22 | Inrush Current | Amps for Secs
23 | Rated full load current | To be Specified by the Bidder
a) H.V.
b) L.V.
24 | Tap Changer
| a) Type | OLTC
| b) Tappings | ­10% to + 10% Taps in Steps of 1.25 % (Typ)
25 | Features of RTCC Panel
a) | Auto Manual Selection | Required
b) | Raise / Lower Push Buttons | Required
c) | AVR | Required
d) | Tap position indicator | Required
e) | Tap change in progress indicating Lamp | Required
26 | Temp. rise over ambient 45 deg.
| a) Windings by Resistance | 45° C
| b) Top oil by Thermometer | 50° C
27 | Terminal Arrangement
| a) H V - (Cable Box ) | Air insulated Disconnecting Chamber (outdoor) to receive 1R x 3C x 240 Sq.mm 33 KV, Al. XLPE with Earth Cable.
| b) L V - (Cable Box ) | Air insulated Disconnecting Chamber (outdoor) to receive 1R x 3C x 240 Sq.mm 11 KV, Al. XLPE with Earth Cable.
28 | Neutral Terminal Arrangement | Cable termination
29 | CTS | 4000/1A (REF) , Class PS CT for Neutral and shall be supplied by Transformer Supplier
30 | % impedance | Considering lowest losses As per IEC Tolerance
31 | Losses | To be specified by the bidder
a) No load losses (KW) at rated Voltage & Freq.
b) Load Losses :-
(i) At 100%Load
(ii) At 50% Load
32 | Flux Density
33 | Regulation
a) | At Unity PF
At 100% Load
At 75% Load
At 50% Load
b) | At 0.8 PF
At 100% Load
At 75% Load
At 50% Load
34 | Efficiency
At 100% Load
At 75% Load
At 50% Load
General Information
1 | Physical Dimensions
a) | Length | mm
b) | Width | mm
c) | Height | mm
2 | Thickness
a) | Wall | mm
b) | Base | mm
c) | Cover | mm
3 | Weight
a) | Weight of core & windings | Kg
b) | Tank & Fitting | Kg
c) | Coolant | Kg
d) | Total Weight | Kg
4 | Oil Quantities
a) | Tank | Liters
b) | Conservator | Liters
c) | Disconnecting chamber | Liters
5 | Confirmation of prescribed tests
6 | Factory acceptance test
38 | NGR 33 KV and 11KV
38.1 | Name of Manufacturer
38.2 | Type
38.3 | Resistance material
38.4 | Voltage
38.5 | Rated Current
38.6 | Rated Duty
38.7 | Total Resistance of resistor
38.8 | Max. allowable temp. rise
38.9 | Service
38.1 | Degree of protection
38.11 | xi. Weight of complete NGR
38.12 | xii. Reference Standard
38.13 | Enclosure material & Thickness
38.14 | Max. overall dimensions
38.15 | Test Voltage (withstand value)

## Annex II B LT trans
ANNEXURE II B TECHNICAL DATA SHEET FOR LT TRANSFORMER DOC NO KAPL/BDP/SR/1482
KARNATAKA ANTIBIOTICS AND PHARMACEUTICAL LTD |  |  |  | DOSHI CONSULTANT PVT LTD
S.No. | Description | DCPl Specification | Vendor to provide data | Remark
Technical Specific
1 | Manufacturer's name and address
2 | Rated KVA | 3Nos. X 2500 KVA
2 | Standard Applicable | Distribution
3 | Ref. standards | IS 1180
4 | Installation (Indoor / Outdoor) | Outdoor
5 | Vector Group | Dyn11
6 | Frequency | 50 Hz
7 | Voltage Ratio | 33/0.415 KV
8 | Winding Material | Copper
9 | Winding Connection | Delta/ Star
Primary/Secondary
10 | Insulation | Class A Uniform
11 | Duty Cycle | Continuous
12 | Degree of Protection | IP55
13 | Cooling System | ONAN
14 | Short Circuit Level at 33 KV | 26.3KA fro 1 Sec.
15 | Rated Primary Voltage | 33 KV
16 | Supply Neutral | Solidly Earthed
17 | Highest System Voltage for Primary | 36 KV
18 | Rated Secondary Voltage (at No­load) | 415 Volts
19 | Supply Neutral | Solidly Earthed
20 | Noise Level | 75 dB(A)-1 Meter(Maximum)
21 | X/R Ratio
22 | Inrush Current | Amps for Secs
23 | Rated full load current | To be Specified by the Bidder
a) H.V.
b) L.V.
24 | Tap Changer
| a) Type | OLTC
| b) Tappings | ­10% to + 10% Taps in Steps of 1.25 % (Typ)
25 | Features of RTCC Panel
a) | Auto Manual Selection | Required
b) | Raise / Lower Push Buttons | Required
c) | AVR | Required
d) | Tap position indicator | Required
e) | Tap change in progress indicating Lamp | Required
26 | Temp. rise over ambient 45 deg.
| a) Windings by Resistance | 45° C
| b) Top oil by Thermometer | 50° C
27 | Terminal Arrangement
| a) H V - (Cable Box / bare Bushuig) | Air insulated Disconnecting Chamber (outdoor) to receive 1R x 3C x 240 Sq.mm 33 KV, Al. XLPE with Earth Cable.
| b) LV - Bbusbar Duct connection | 4000A LV Busduct
28 | Neutral Terminal Arrangement | Bushing/ Bus Bar
29 | CTS | 4000/1A (REF) , Class PS CT for Neutral and shall be supplied by Transformer Supplier
30 | % impedance | 7.25 % As per IEC Tolerance
31 | Losses | To be specified by the bidder
a) No load losses (KW) at rated Voltage & Freq.
b) Load Losses :-
(i) At 100%Load
(ii) At 50% Load
32 | Flux Density
33 | Regulation
a) | At Unity PF
At 100% Load
At 75% Load
At 50% Load
b) | At 0.8 PF
At 100% Load
At 75% Load
At 50% Load
34 | Efficiency
At 100% Load
At 75% Load
At 50% Load
General Information
1 | Physical Dimensions
a) | Length | mm
b) | Width | mm
c) | Height | mm
2 | Thickness
a) | Wall | mm
b) | Base | mm
c) | Cover | mm
3 | Weight
a) | Weight of core & windings | Kg
b) | Tank & Fitting | Kg
c) | Coolant | Kg
d) | Total Weight | Kg
4 | Oil Quantities
a) | Tank | Liters
b) | Conservator | Liters
c) | Disconnecting chamber | Liters
5 | Confirmation of prescribed tests
6 | Factory acceptance test

## Annex II C HT switch gear
ANNEXURE II C TECHNICAL DATA SHEET FOR HT SWITCH GEAR DOC NO KAPL/BDP/CG/_______
KARNATAKA ANTIBIOTICS AND PHARMACEUTICAL LTD |  |  |  | DOSHI CONSULTANT PVT LTD
S.No. | Description | DCPl Specification | Vendor to provide data | Remark
33KV VCB (ICOG) panel
Basic VCB Unit
| Make | To be Specified by Bidder
| Type | Horizontal Draw Out- EDO
| Rating | 33KV, 1250A VCB ICOG
| Short circuit level | 25 KA for 3 Sec
| Operating Mechanism | Spring charged motorized with additional manual operation facility
| Bus Bar | Copper of 1.2 A/Sq.mm Current Density
Current transformer
| Type | Resin cast (Dual core)
| Ratio | As per SLD
| Burden | 15 VA
Accuracy class
| Metering | Class 1
| Protection | Class 5P20
Potential Transformer
| Type | Resin cast
| Ratio | 33 KV/√3 : 110 V/ √3
| Burden | 100 VA
| Accuracy class | 1
Terminal Arrangement
| Incoming | Cable Box (Suitable for 2Nosx3C* 300Sq.mm, Al. XLPE Cable)
(Cable / Bare Bushing)
| Outgoing | Cable Box (Suitable for 2Nosx3C* 300Sq.mm, Al. XLPE Cable)
(Cable / Bare Bushing)
Metering
| Multi-Function Meter / Demand Controller | Required As per SLD
| Indication | Required
| Breaker ON/ OFF / TRIP | LED Lamps
| Spring Charged | LED Lamps
| Trip Circuit healthy | Common scheme with Lamp and Push buttons
| Operation counter | Mechanical
| Spring status indicator | Mechanical
| Breaker Status Indicator | Mechanical ON / OFF Indication
8 | Protection Scheme
| 51/51N, 50/50N, 27, 59, 64, 95, 97 | Required In HT VCB FEEDER
| Anti pumping relay | Required
9 | General
| Duty (Indoor / Outdoor) | Indoor (Subjected to Approval)
| Breaker control switch | TNC
| Local manual emergency trip push | Required
| Panel Heater | Required
| Panel Light & Plug Socket | Required
| Closing coil assembly | 24V/30V /110V DC
| Trip coil assembly | 24V /30V/110V DC
| Power pack | 230 V AC input, 24V/30V/110V DC output
| Degree of Protection | To be specified by the bidder
| Interlocking & safety shutters | As provided in detailed specification
| Earth Bus | Panel back bottom
| Alarm scheme | As provided in detailed specification
Physical Dimensions
Weight
33KV VCB panel
Basic VCB Unit
| Make | To be Specified by Bidder
| Type | Horizontal Draw Out- EDO
| Rating | 33KV, 1250A ICx1No + 1250A O/Gx6Nos
| Short circuit level | 25 KA for 3 Sec
| Operating Mechanism | Spring charged motorized with additional manual operation facility
| Bus Bar | Copper of 1.2 A/Sq.mm Current Density
Current transformer
| Type | Resin cast (Dual core)
| Ratio | As per SLD
| Burden | 15 VA
Accuracy class
| Metering | Class 1
| Protection | Class 5P20
Potential Transformer
| Type | Resin cast
| Ratio | 33 KV/√3 : 110 V/ √3
| Burden | 100 VA
| Accuracy class | 1
Terminal Arrangement
| Incoming | Cable Box (Suitable for 2Nosx3C* 300Sq.mm, Al. XLPE Cable)
(Cable / Bare Bushing)
| Outgoing | Cable Box (Suitable for 3C* 240Sq.mm, Al. XLPE Cable)
(Cable / Bare Bushing)
Metering
| Multi-Function Meter / Demand Controller | Required As per SLD
| Indication | Required
| Breaker ON/ OFF / TRIP | LED Lamps
| Spring Charged | LED Lamps
| Trip Circuit healthy | Common scheme with Lamp and Push buttons
| Operation counter | Mechanical
| Spring status indicator | Mechanical
| Breaker Status Indicator | Mechanical ON / OFF Indication
8 | Protection Scheme
| 51/51N, 50/50N, 27, 59, 64, 97 | Required In HT VCB INCOMER FEEDER
| 51/51N, 50/50N, 86, 95, 63-O, 63-T, 63-X, 27, 59 | Required In HT VCB OUTGOING FEEDER
| Anti pumping relay | Required
9 | General
| Duty (Indoor / Outdoor) | Indoor (Subjected to Approval)
| Breaker control switch | TNC
| Local manual emergency trip push | Required
| Panel Heater | Required
| Panel Light & Plug Socket | Required
| Closing coil assembly | 24V/30V /110V DC
| Trip coil assembly | 24V /30V/110V DC
| Power pack | 230 V AC input, 24V/30V/110V DC output
| Degree of Protection | To be specified by the bidder
| Interlocking & safety shutters | As provided in detailed specification
| Earth Bus | Panel back bottom
| Alarm scheme | As provided in detailed specification
Physical Dimensions
Weight
11KV VCB panel 1
Basic VCB Unit
| Make | To be Specified by Bidder
| Type | Horizontal Draw Out- EDO
| Rating | 11KV, 1250A ICx3Nos + 630A O/Gx2Nos + 1250A O/Gx1Nos+ 1250A B/Cx2Nos with bus PT 2Nos.
| Short circuit level | 21 KA for 3 Sec
| Operating Mechanism | Spring charged motorized with additional manual operation facility
| Bus Bar | Copper of 1.2 A/Sq.mm Current Density
Current transformer
| Type | Resin cast (Dual core)
| Ratio | As per SLD
| Burden | 15 VA
Accuracy class
| Metering | Class 1
| Protection | Class 5P10
Potential Transformer
| Type | Resin cast
| Ratio | 11 KV/√3 : 110 V/ √3
| Burden | 100 VA
| Accuracy class | 1
Terminal Arrangement
| Incoming | Cable Box (Suitable for 3C* 240Sq.mm, Al. XLPE Cable)
(Cable / Bare Bushing)
| Outgoing | Cable Box (Suitable for 3C* 240Sq.mm, Al. XLPE Cable)
(Cable / Bare Bushing)
Metering
| Multi-Function Meter / Demand Controller | Required As per SLD
| Indication | Required
| Breaker ON/ OFF / TRIP | LED Lamps
| Spring Charged | LED Lamps
| Trip Circuit healthy | Common scheme with Lamp and Push buttons
| Operation counter | Mechanical
| Spring status indicator | Mechanical
| Breaker Status Indicator | Mechanical ON / OFF Indication
8 | Protection Scheme
| 51/51N, 50/50N, 27, 59, 64, 95,97 | Required In HT VCB INCOMER FEEDER
| 51/51N, 50/50N, 27, 59, 64, 95 | Required In HT VCB OUTGOING FEEDER
| Anti pumping relay | Required
9 | General
| Duty (Indoor / Outdoor) | Indoor (Subjected to Approval)
| Breaker control switch | TNC
| Local manual emergency trip push | Required
| Panel Heater | Required
| Panel Light & Plug Socket | Required
| Closing coil assembly | 24V/30V /110V DC
| Trip coil assembly | 24V /30V/110V DC
| Power pack | 230 V AC input, 24V/30V/110V DC output
| Degree of Protection | To be specified by the bidder
| Interlocking & safety shutters | As provided in detailed specification
| Earth Bus | Panel back bottom
| Alarm scheme | As provided in detailed specification
Physical Dimensions
Weight
11KV VCB panel 2
Basic VCB Unit
| Make | To be Specified by Bidder
| Type | Horizontal Draw Out- EDO
| Rating | 11KV, 1250A ICx1Nos + 630A O/Gx6Nos
| Short circuit level | 21 KA for 3 Sec
| Operating Mechanism | Spring charged motorized with additional manual operation facility
| Bus Bar | Copper of 1.2 A/Sq.mm Current Density
Current transformer
| Type | Resin cast (Dual core)
| Ratio | As per SLD
| Burden | 15 VA
Accuracy class
| Metering | Class 1
| Protection | Class 5P10
Potential Transformer
| Type | Resin cast
| Ratio | 11 KV/√3 : 110 V/ √3
| Burden | 100 VA
| Accuracy class | 1
Terminal Arrangement
| Incoming | Cable Box (Suitable for 3C* 240Sq.mm, Al. XLPE Cable)
(Cable / Bare Bushing)
| Outgoing | Cable Box (Suitable for 3C* 185Sq.mm, Al. XLPE Cable)
(Cable / Bare Bushing)
Metering
| Multi-Function Meter / Demand Controller | Required As per SLD
| Indication | Required
| Breaker ON/ OFF / TRIP | LED Lamps
| Spring Charged | LED Lamps
| Trip Circuit healthy | Common scheme with Lamp and Push buttons
| Operation counter | Mechanical
| Spring status indicator | Mechanical
| Breaker Status Indicator | Mechanical ON / OFF Indication
8 | Protection Scheme
| 51/51N, 50/50N, 27, 59, 64, 95,97 | Required In HT VCB INCOMER FEEDER
| 51/51N, 50/50N, 27, 59, 64, 95 | Required In HT VCB OUTGOING FEEDER
| Anti pumping relay | Required
9 | General
| Duty (Indoor / Outdoor) | Indoor (Subjected to Approval)
| Breaker control switch | TNC
| Local manual emergency trip push | Required
| Panel Heater | Required
| Panel Light & Plug Socket | Required
| Closing coil assembly | 24V/30V /110V DC
| Trip coil assembly | 24V /30V/110V DC
| Power pack | 230 V AC input, 24V/30V/110V DC output
| Degree of Protection | To be specified by the bidder
| Interlocking & safety shutters | As provided in detailed specification
| Earth Bus | Panel back bottom
| Alarm scheme | As provided in detailed specification
Physical Dimensions
Weight
NOTE:Please provide the following information
1 | Physical Dimensions
2 | Weight
3 | Copy of routine tests certificates
4 | Type test certificate & Operational Manual of all equipments
5 | Factory acceptance test
6 | 3 sets approval drawings.
7 | Guarantee Certificate
8 | Details of applicable taxes & Duties
9 | Commissioning at site should be inclusive.

## Annex II D APFC
ANNEXURE II D TECHNICAL DATA SHEET FOR 11KV CAPACITOR/APFC PANEL DOC NO KAPL/BDP/SR/1482
KARNATAKA ANTIBIOTICS AND PHARMACEUTICAL LTD |  |  |  | DOSHI CONSULTANT PVT LTD
S.No. | Description | DCPLSpecification | Vendor to provide data | Remark
Technical Specific
A | Manufacturer's name and address
B | Reference standards | IS 13925 Part 1 1998
C | Type | HT CAP PANEL
D | System voltage (KV) | 11KV
E | CAPACITOR PANEL
1 | Rated Output of capacitor Panel | 2000 KVAR (Designed @2737 KVAR)
2 | Rated voltage of capacitor Bank Panel | 11 KV (Designed @ 12.87 KV)
3 | Rated Current Of Capacitor Bank Panel
4 | Type of Panel | APFC Panel
5 | No of Phases & Frequency | 3 & 50 Hz
6 | Bus Bar/ Earth Bus Bar
7 | Type of switching | Auto / Manual
8 | Enclosure | Cubical
9 | Material of Cubical and thickness | CRCA & 2.5mm/2 mm
10 | Electrical clearance in the bank
a | Phase to phase
b | Phase to earth
12 | STEP DETAILS
a | No. of Steps | 6
b | Size of each Step | 333.33 KVAR (Designed @ 456.45 KVAR)
c | Rated current of each step | 17.49 Amp
d | Rated Voltage of each step | 11 KV (Designed @ 12.87 KV)
e | Rated Capacitance of each step
f | Switching Device | Vaccum contactor Rated at 400 Amps, 12 KV, 3 Pole
g | Fuse protection | Provided through 11 KV HRC Fuses for each step
F | CAPACITOR UNIT
a | Rated Output of capacitor Unit
b | Rated voltage of capacitor Unit
c | Rated Current Of capacitor Unit
d | No of Phases & No of bushings | 1 & 2
e | Capacitance of Unit | 8.77 MFD
f | Type of solid dielectric - | POLYPROPYLENE FILM
g | Type of impregnating medium | NON PCB-NON HAZARDOUS CAPACITOR GRADE PXE OIL
h | Type of conductor
i | Material of container and thickness | CRCA & 2 MM
j | Bushings | 12 KV Weldable Type
k | Material of bushing
OTHER PARAMETERS
G | PERMISSIBLE OVERLOADS
a | Voltage | 110% OF RATED VOLTAGE
b | Current | 130% OF RATED CURRENT
c | Output KVAR | 130% OF RATED KVAR
H | INSULATION LEVEL
a | Power Frequency Test Voltage | KV RMS 28
b | Impulse Voltage KV Peak | PEAK 75
I | Dielectric Loss
J | Discharge Device
K | Discharge Time
L | Temperature Category | 50 °C
M | AIR CORED SERIES REACTOR
a | Make | Amar/eqv
b | Reactance | 6% of capacitive Reactance
c | KVAR Per Phase per step
d | Current
e | Voltage | 11 KV
f | Class of Insulation | F
g | Winding Material | Aluminum
h | Voltage | Drop 381 Volts
N | ISOLATOR
a | Make | HTS/PSPL
b | Type
c | Voltage | 11 KV
d | Current
e | Short time ratings | 25 KA for 1 sec
f | No of poles | 3 Pole
g | Control Voltage/Aux Contacts | 230 V AC/2NO+2NC
O | VACCUM CONTACTOR
a | Make
b | Voltage | 11 KV
c | Current
d | No of poles | 3 Pole
e | Control Voltage | 230 V AC
P | RVT
a | Make
b | Type
c | Burden | 50 VA
d | Acc. Class / Protection | Class 1 /5PR
e | Connection | Star/Star-Open delta 11 KV/110V-190 V
Q | CURRENT TRANSFORMER
a | Make
b | Type
c | Burden | 15 VA
d | Acc. Class / Protection | Class 1 /5P10
e | Ratio | 50/5-5