## Annexure-III
ANNEXURE III PRICE BID HIGH TENSION ELECTRIFICATION WORK DOC NO KAPL/BDP/CG/1482
KARNATAKA ANTIBIOTICS AND PHARMACEUTICAL LTD | [7 empty] | DOSHI CONSULTANT PVT LTD
BILL OF QUANTITY
SR .NO. | DESCRIPTION | UNIT | OFFERED MAKE CONSIDER AS PER MAKE LIST | QUANTITY | UNIT PRICE |  | TOTAL AMOUNT |  | REMARK
|  |  |  | COMMON | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
1 | PRICE
Supply, Installation & Commissioning HIGH TENSION ELECTRIFICATION WORK in accordance with technical specification as mention in bill of quantity and requirement laid down Section VIII of this tender and technical data Sheet.
A. | H.T. SWITCH YARD - 1
All the system shall be as per dwg & specifications and as per IE rules.
33KV 4-Pole Structure
Supply, installation testing and commissioning of various items for 33KV, 4 Pole receiving station as per IE rules. complete with following equipment to be supplied & installed complete with inter connections & all hardware, consumables, welding rods etc.
| Supply, Installation, Testing & Commissioning of 4 Pole Structure fabricated from using 4 nos 13mtr ISH Beam 152x152mm, and all cross members with ISMC-100, channels, all C-clamps made of 50x8/75x10 duly painted with 1 coat red oxide and 2 coats of Aluminium paint. This is to accommodate the AB Switch , DO Fuse set & L.A. Set and CT/PT unit . Complete work has to be executed as per dwg & specifications. The work also includes providing help in installation of CT/ PT unit & Meter Unit of Electricity Board etc. The job shall include interconnection with electricity board 4-Pole structure Including excavation of soil for foundation, making of foundation (1:2:4) for poles, complete in all respects. This shall also include supply and fixing of stay wire and their supports including foundation work for structure and stay wire supports. | [7 empty] | As per Electricity Board
A.1 | SUPPLY OF MATERIALS REQUIRED FOR INSTALLATION OF 33 KV SUB STATION
A.1.1 | Supply of AAAC DOG conductor required for installation of new 33 KV substation | mtr |  | 175 |  |  | 0 | 0
A.1.2 | DC Cross Arms size 100mmX 5mtr length | Nos |  | 14 |  |  | 0 | 0
A.1.3 | Flat clamp type A & B | Nos |  | 100 |  |  | 0 | 0
A.1.4 | Hard ware Nut & Bolts etc.high tensile strength | kg |  | 60 |  |  | 0 | 0
A.1.5 | Coil Earthing Materials with 8 swg G.I.wire 115 turns,50 mm dia | Each |  | Optional item. rate to be quoted
A.1.6 | 33 KV Pin Insulators polymers with Hardware | Nos |  | 6 |  |  | 0 | 0
A.1.7 | 33 KV Disc Insulators with Hardware | Nos |  | 6 |  |  | 0 | 0
A.1.8 | Anti climbing device on pole as per IE Rule | Nos |  | 4 |  |  | 0 | 0
A.1.9 | 12core x 2.5 sq mm armoured copper cable | Mtr |  | Optional item. rate to be quoted
A.1.10 | Guarding supports | Nos |  | 4 |  |  | 0 | 0
A.1.11 | CT/PT ME , Cable, MSeal, TTB with accessories | SET |  | 1 |  |  | 0 | 0
A.1.12 | Tri Vector Meter Box with accessories | SET |  | 1 |  |  | 0 | 0
A.1.13 | Supply & installation of metering shed | Nos. |  | 1 |  |  | 0 | 0
A.1.14 | HT clamp for CT’S | Nos |  | 15 |  |  | 0 | 0
A.1.15 | H Beam 152x152mm (@37.5 Kg/mtr) with two coats of epoxy primer and two coats of finsihed epoxy paint | KG |  | 2500 |  |  | 0 | 0
A.1.16 | PG Clamps | Nos |  | 18 |  |  | 0 | 0
A.1.17 | Installation,Testing & Commissioning of Maintenance free Chemical earthing of Dual electrode base strip in technology. 3mtr. long with Outer dia. of 77-80mm dia of 80-120 micron galvanization and wall thickness of pipe. Insider Strip 50 *10mm, strip should be welded & connected at both end cap of pipe. Earthing electrode to be filled & compressed with the highly conductive non corrosive graphite based compound material with sealing at both end with lead terminals of 65X5 mm at top. Along with the 50Kg of earth enhancing compound (natural minerals like silica, Alumina, iron, calcium, carbon).. The Chemical compound should be tested and certified by BIS accredited laboratory. Ph value should be 7.5. The earth pits shall have a test ling for checking of earth values. This includes supply & fixing of watering pipe & strip 65X5 mm brought out up to ground level. [ Earthing Should be tested for short circuit current rating of 40kA for 1 Sec. from approved laboratory. As per IS 3043. | Nos |  | 30 |  |  | 0 | 0
A.1.18 | Installation,Testing & Commissioning of Maintenance free Chemical earthing of Dual electrode base strip in technology. 3mtr. long with Outer dia. of 77-80mm dia of 250 micron Copper bonded and wall thickness of pipe. Insider cu. bonded Strip 50 *10mm, strip should be welded & connected at both end cap of pipe. Earthing electrode to be filled & compressed with the highly conductive non corrosive graphite based compound material with sealing at both end with lead terminals of 50X10 mm at top. Along with the 50Kg of earth enhancing compound (natural minerals like silica, Alumina, iron, calcium, carbon). The Chemical compound should be tested and certified by BIS accredited laboratory. Ph value should be 7.5. The earth pits shall have a test ling for checking of earth values. This includes supply & fixing of watering pipe & strip 65X5 mm brought out up to ground level. [ Earthong Should be tested for short circuit current rating of 40kA for 1 Sec. from approved laboratory. As per IS 3043. | Nos |  | 14 |  |  | 0 | 0
G.I Strip /Wire Earthing
Supply & laying of Hot Dipped G.I. (80 micron) earthing strip/wire.
A.1.18.1 | 75 x 10 mm GI Strip (For 33/11KV HT / Trafo Body) | Mtr. |  | 100
A.1.18.2 | 50 x 5 mm GI Strip (For Tapping, HT / Trafo Body) | Mtr. |  | 150
A.1.18.3 | 40 x 5mm GI Strip (For Tapping on Panel/ Equipment ) | Mtr. |  | Optional item. rate to be quoted
A.1.18.4 | 25 x 3mm GI Strip (For Tapping on Panel/ Equipment ) | Mtr. |  | 200
A.1.18.5 | 8 SWG Bare GI Wire | Mtr. |  | Optional item. rate to be quoted
A.1.18.6 | 10 SWG Bare GI. Wire | Mtr. |  | Optional item. rate to be quoted
Supply & Laying of EC GRADE 'CU' Strip /Earthing Wire. Including fixing at equipment end (with Insulators & other required hard wares)
A.1.18.7 | 50 x 5 mm Cu Strip (For Neutral / Electronic Earthing Grid ) | Mtr. |  | 100
A.1.18.8 | 40 x 5 mm Cu Strip | Mtr. |  | Optional item. rate to be quoted
A.1.18.9 | 25 x 3mm Cu Strip (For Tapping of Neutral/Static/Electronic Earthing) | Mtr. |  | 200
A.1.18.10 | 120SQ.MM. Cu. Flexi Wire | Mtr. |  | 50
A.1.19 | 33 KV Copper XLPE cable 3CX300 sqmm | Mtrs. |  | 50 |  |  | 0 | 0
A.1.20 | 33 KV Alluminum XLPE cable 3CX400 sqmm | Mtrs. |  | Optional item. rate to be quoted
A.1.21 | Termination of 33 KV Copper XLPE cable 3CX300 sqmm Outdoor Type | Set |  | 2 |  |  | 0 | 0
A.1.22 | Termination of 33 KV Alluminum XLPE cable 3CX400 sqmm Outdoor Type | Set |  | Optional item. rate to be quoted
A.1.23 | Termination of 33 KV Copper XLPE cable 3CX300 sqmm Indoor type | Set |  | 1 |  |  | 0 | 0
A.1.24 | Termination of 33 KV Alluminum XLPE cable 3CX400 sqmm Indoor type | Set |  | Optional item. rate to be quoted
A.1.25 | stay set | Nos |  | 2 |  |  | 0 | 0
A.1.26 | Out door 33 KV AB Switch 400amp | nos |  | 1 |  |  | 0 | 0
A.1.27 | 33 KV Drop out fuse(DO) 400 amps Sets complete with insulators & hard ware | nos |  | 3 |  |  | 0 | 0
A.1.28 | Lighting arrester 29 KV, | set |  | 1 |  |  | 0 | 0
A.1.29 | GI strip size 50X5 | Mtrs |  | 150 |  |  | 0 | 0
A.1.30 | 32X5 mm Copper Strip for LA and Neutral earth | Mtrs |  | 75 |  |  | 0 | 0
A.1.31 | Concreting of H Beam and stay (20 mm / 25 mm) @ 0.3 cmt. per stay(apprx) | Cmt |  | 4.5 |  |  | 0 | 0
A.1.32 | Supply, Loading, Unloading, Shifting, Installation, Testing & Commissioning of 33kV HT CICO Panel - Outdoor type [1No. VCB with Cable in & Cable out.] (As per Dwgs no - 626/KAPL/HT-SD/EL-600) | nos |  | 1 |  |  | 0 | 0
B | HT PANEL & CABLE | [5 empty] | 0 | 0
B.1 | 33 KV LINE UP TO TRANSFORMERS
| Supply, Loading, Unloading, Shifting, Installation, Testing & Commissioning of 33kV HT VCB Panel - Indoor [1No.VCB Incoming & 5No. Outgoing (Present) + 1 Outgoing (Future)] (As per Dwgs no - 626/KAPL/HT-SD/EL-601) | nos. |  | 1
B.1.1 | Supply of 33 KV Alluminum XLPE cable 3CX300 sq.mm. (From 33KV ICOG to 33KV VCB panel near LT panel room ) | mtr |  | 1050 |  |  | 0 | 0
B.1.2 | Supply of 33 KV Alluminum XLPE cable 3CX240 sq.mm.(From 33KV VCB panel to LT transformer ) | mtr |  | 150 |  |  | 0 | 0
B.1.3 | Supply & making of Cable end termination of Termination of 33 KV XLPE cable 3CX300 sq.mm ( gland,lugs etc.) | set |  | 6 |  |  | 0 | 0
B.1.4 | Supply & making of Cable end termination of Termination of 33 KV XLPE cable 3CX240 sq.mm ( gland,lugs etc.) | set |  | 10 |  |  | 0 | 0
B.1.5 | Supply, Loading, Unloading, Shifting, Installation, Testing & Commissioning of 2.5MVA ,33KV/ 0.433KV , 3 Phase, 50 Hz Oil type copper wound transformer . The electrical contractor shall execute all work of interconnection of transformer. The Transformer is with OLTC and installation, testing & commissioning of RTCC panel shall be a part of the scope of work of bidder. | No's |  | 3 |  |  | 0 | 0 | As per Electricity Board
B.1.6 | Supply, Loading, Unloading, Shifting, Installation, Testing & Commissioning of 8 MVA ,33KV/ 11KV , 3 Phase, 50 Hz Oil type copper wound transformer . The electrical contractor shall execute all work of interconnection of transformer. The Transformer is with OLTC and installation, testing & commissioning of RTCC panel shall be a part of the scope of work of bidder. | No's |  | 2 |  |  | 0 | 0 | As per Electricity Board
B.2 | 11KV,HT COMPRESSOR PANEL1 (IN PANEL ROOM)
B.2.1 | Supply, Loading, Unloading, Shifting, Installation, Testing & Commissioning of 11kV HT VCB Panel - Indoor [3Nos.VCB Incoming & 4No. Outgoing + 2Nos. Bus-Coupler] (As per Dwgs no - 626/KAPL/HT-SD/EL-602A) | nos. |  | 1
B.2.2 | 11KV, Capacitor Bank 2000KVAR with auto correction panel | set. |  | 2
B.2.3 | Supply of 11 KV XLPE cable 3CX240 sq.mm. (from 11KV VCB Panel to capacitor bank ) | mtr |  | 50 |  |  | 0 | 0
B.2.4 | Supply & making of Cable end termination of Termination of 11 KV XLPE cable 3CX240 sq.mm ( gland,lugs etc.) | set |  | 4 |  |  | 0 | 0
B.2.5 | DCDB Battery & Battery charger 110V/30V/24V DC (FOR 11KV & 33KV PANEL CONTROL CIRCUIT). Battery Backup 30Minutes. | set |  | 2
B.2 | 11KV,HT COMPRESSOR PANEL2 (IN UTILITY ROOM)
B.2.1 | Supply, Loading, Unloading, Shifting, Installation, Testing & Commissioning of 11kV HT VCB Panel - Indoor [2Nos.VCB Incoming , 6No. Outgoing & 1No. Bus-coupler] (As per Dwgs no - 626/KAPL/HT-SD/EL-602B) | nos. |  | 1
B.2.3 | Supply of 11 KV XLPE cable 3CX240 sq.mm. (From 11KV PANEL IN PANEL ROOM to 11KV Panel in utility room) | mtr |  | 450 |  |  | 0 | 0
B.2.3 | Supply of 11 KV XLPE cable 3CX 240 sq.mm. (From VCB to COMPRESSOR ) | mtr |  | 200
B.2.4 | Supply & making of Cable end termination of Termination of 11 KV XLPE cable 3CX240 sq.mm ( gland,lugs etc.) | set |  | 8 |  |  | 0 | 0
B.2.4 | Supply & making of Cable end termination of Termination of 11 KV XLPE cable 3CX185 sq.mm ( gland,lugs etc.) | set |  | 12
B.2.5 | Battery & Battery charger 110V/30V/24V DC (for 11KV panel control circuit) | nos. |  | 1
1.1KV Grade XLPE control cable (multi core with multi colour), Circular stranded (rm) annealed stranded Copper Conductor PVC insulated and provided with a common covering of PVC inner sheath, Un-armoured and overall PVC sheathed of type ST2 PVC compound flexible Confirming to IEC 60502 (Flame Retardant (FR), Flame retardant Low Smoke (FRLS), to suit a variety of environment and fire risk condition). Type YY:
| 2C x 2.5 Sqmm PVC Cu.- For Control | Mtr. |  | 200
| 3C x 2.5 Sqmm PVC Cu.- For Control | Mtr. |  | 500
| 7C x 2.5 Sqmm PVC Cu.- For Control | Mtr. |  | Optional item. rate to be quoted
| 12C x 2.5 Sqmm PVC Cu.- For Control | Mtr. |  | 500
| 12C x 1.5 Sqmm PVC Cu.- For Control | Mtr. |  | 200
| 12C x 1 Sqmm PVC Cu.- For Control | Mtr. |  | 200
| 24C x 2.5 Sqmm PVC Cu.- For Control | Mtr. |  | Optional item. rate to be quoted
C.2.1 | Supply & Installation of Single Compression Type Cable Glands, Cable Lugs, heat shrinkable sleeves on long ends, crimping paste etc. the work includes testing & commissioning of cables, meggering values & submitting reports of tests. One set includes termination of all cores of one end only.
| 2C x 2.5 Sqmm XLPE Cu.- For Control | Set |  | 10
| 3C x 2.5 Sqmm XLPE Cu.- For Control | Set |  | 20
| 7C x 2.5 Sqmm XLPE Cu.- For Control | Set |  | 1
| 12C x 2.5 Sqmm XLPE Cu.- For Control | Set |  | 20
| 12C x 1.5 Sqmm PVC Cu.- For Control | Set |  | 10
| 12C x 1 Sqmm PVC Cu.- For Control | Set |  | 10
| 24C x 2.5 Sqmm XLPE Cu.- For Control | Set |  | 1
C | SAFETY EQUIPMENTS AND MISC ITEMS | [5 empty] | 0 | 0 | 0
C.1 | Supply & Fixing of Caution Boards. | No's |  | 3 |  |  | 0 | 0
C.2 | Supply & Fixing of Shock Treatment Chart in English & Hindi Language fixed on Ply & covered with 3mm thick plain glass. | No's |  | 3 |  |  | 0 | 0
C.3 | Supply of 33KV hand gloves duly tested. | Pair |  | 2 |  |  | 0 | 0
C.4 | Supply of 11KV hand gloves duly tested. | Pair |  | 3 |  |  | 0 | 0
C.5 | Supply of 33KV DO Isolator Rod. | No. |  | 2 |  |  | 0 | 0
C.6 | Supply of Filled First Aid box complete with all standard medicines as per I.E rules. | No. |  | 2 |  |  | 0 | 0
C.7 | Supply & Fixing of HT Rubber Matfor 33KV as per IS 15652 (standarded size) | Sq mtr |  | 25 |  |  | 0 | 0
C.8 | Supply & Fixing of HT Rubber Mat for11KV as per IS 15652 (standarded size) | Sq mtr |  | 40 |  |  | 0 | 0
C.9 | Supply, Filling & fixing of following type of fire extinguishers in electrical room | [5 empty] | 0 | 0 | 0
C.10 | a) CO2 type fire extinguisher 5 kg | No. |  | 2 |  |  | 0 | 0
C.11 | b). Dry Powder type 5 Kg. | No. |  | 2 |  |  | 0 | 0
| Supply & Filling & fixing of following type of safety items in electrical room | [5 empty] | 0 | 0
C.11 | a) Sand bucket stand with 5 nos. MS. Buckets. | Set |  | 5 |  |  | 0 | 0
Supplying and installing following size of perforated Hot DippedGalvanised Iron cable tray (galvanisation thickness not less than50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
C.12 | 100 mm width X 50 mm depth X 1.6 mm thickness | Meter |  | 100
C.13 | 300 mm width X 100 mm depth X 2.0 mm thickness | Meter |  | 80
| Fabrication /erection of cable tray supports/ Clamps from M.S. equal angle and strips as per drawing and specifications. Work also includes arranging consumables, grinding / filling of all welded joints, painting with one coat of anticorrosive paint & 2 coat of approved colour Synthetic enamel paint. | Kgs. |  | 500
D | SUPPLY AND INSTALLATION OF FENCING & CIVIL MATERIAL. | [5 empty] | 0 | 0
D.1 | Supply & Installation of Fencing angle MS 65X65X5 (up to height 3 mtr) | Kg |  | 500 |  |  | 0 | 0
D. 2 | Supply & Installation of Fencing chain link of GI wire 10SWG 2.5Meter height | Sq Mtr |  | 250
D.2 | Supply & Installation of MS Gate with fabrication with two coats of epoxy primer and two coats of finsihed epoxy paint | kg |  | 600 |  |  | 0 | 0
D.3 | Supply & install Of earth chamber. Civil Work only | nos. |  | 44 |  |  | 0 | 0
D.4 | Supply & spreading of Gitti/Metal 40mm thik on yard and levelling of yard. | Cu.mtr |  | 15 |  |  | 0 | 0
E. | H.T. SWITCH YARD - 2
All the system shall be as per dwg & specifications and as per IE rules.
33KV 4-Pole Structure
Supply, installation testing and commissioning of various items for 33KV, 4 Pole receiving station as per IE rules. complete with following equipment to be supplied & installed complete with inter connections & all hardware, consumables, welding rods etc.
| Supply, Installation, Testing & Commissioning of 4 Pole Structure fabricated from using 4 nos 13mtr ISH Beam 152x152mm, and all cross members with ISMC-100, channels, all C-clamps made of 50x8/75x10 duly painted with 1 coat red oxide and 2 coats of Aluminium paint. This is to accommodate the AB Switch , DO Fuse set & L.A. Set and CT/PT unit . Complete work has to be executed as per dwg & specifications. The work also includes providing help in installation of CT/ PT unit & Meter Unit of Electricity Board etc. The job shall include interconnection with electricity board 4-Pole structure Including excavation of soil for foundation, making of foundation (1:2:4) for poles, complete in all respects. This shall also include supply and fixing of stay wire and their supports including foundation work for structure and stay wire supports. | [7 empty] | As per Electricity Board
E.1 | SUPPLY OF MATERIALS REQUIRED FOR INSTALLATION OF 33 KV SUB STATION
E.1.1 | Supply of AAAC DOG conductor required for installation of new 33 KV substation | mtr |  | 175 |  |  | 0 | 0
E.1.2 | DC Cross Arms size 100mmX 5mtr length | Nos |  | 14 |  |  | 0 | 0
E.1.3 | Flat clamp type A & B | Nos |  | 100 |  |  | 0 | 0
E.1.4 | Hard ware Nut & Bolts etc.high tensile strength | kg |  | 60 |  |  | 0 | 0
E.1.5 | Coil Earthing Materials with 8 swg G.I.wire 115 turns,50 mm dia | Each |  | Optional item. rate to be quoted
E.1.6 | 33 KV Pin Insulators polymers with Hardware | Nos |  | 6 |  |  | 0 | 0
E.1.7 | 33 KV Disc Insulators with Hardware | Nos |  | 6 |  |  | 0 | 0
E.1.8 | Anti climbing device on pole as per IE Rule | Nos |  | 5 |  |  | 0 | 0
E.1.9 | 12core x 2.5 sq mm armoured copper cable | Mtr |  | Optional item. rate to be quoted
E.1.10 | Guarding supports | Nos |  | 4 |  |  | 0 | 0
E.1.11 | CT/PT ME , Cable, MSeal, TTB with accessories | SET |  | 1 |  |  | 0 | 0
E.1.12 | Tri Vector Meter Box with accessories | SET |  | 1 |  |  | 0 | 0
E.1.13 | Supply & installation of metering shed | Nos. |  | 1 |  |  | 0 | 0
E.1.14 | HT clamp for CT’S | Nos |  | 15 |  |  | 0 | 0
E.1.15 | H Beam 152x152mm (@37.5 Kg/mtr) with two coats of epoxy primer and two coats of finsihed epoxy paint | KG |  | 2500 |  |  | 0 | 0
E.1.16 | PG Clamps | Nos |  | 18 |  |  | 0 | 0
E.1.17 | Installation,Testing & Commissioning of Maintenance free Chemical earthing of Dual electrode base strip in technology. 3mtr. long with Outer dia. of 77-80mm dia of 80-120 micron galvanization and wall thickness of pipe. Insider Strip 50 *10mm, strip should be welded & connected at both end cap of pipe. Earthing electrode to be filled & compressed with the highly conductive non corrosive graphite based compound material with sealing at both end with lead terminals of 65X5 mm at top. Along with the 50Kg of earth enhancing compound (natural minerals like silica, Alumina, iron, calcium, carbon).. The Chemical compound should be tested and certified by BIS accredited laboratory. Ph value should be 7.5. The earth pits shall have a test ling for checking of earth values. This includes supply & fixing of watering pipe & strip 65X5 mm brought out up to ground level. [ Earthing Should be tested for short circuit current rating of 40kA for 1 Sec. from approved laboratory. As per IS 3043. | Nos |  | 4 |  |  | 0 | 0
E.1.18 | Installation,Testing & Commissioning of Maintenance free Chemical earthing of Dual electrode base strip in technology. 3mtr. long with Outer dia. of 77-80mm dia of 250 micron Copper bonded and wall thickness of pipe. Insider cu. bonded Strip 50 *10mm, strip should be welded & connected at both end cap of pipe. Earthing electrode to be filled & compressed with the highly conductive non corrosive graphite based compound material with sealing at both end with lead terminals of 50X10 mm at top. Along with the 50Kg of earth enhancing compound (natural minerals like silica, Alumina, iron, calcium, carbon). The Chemical compound should be tested and certified by BIS accredited laboratory. Ph value should be 7.5. The earth pits shall have a test ling for checking of earth values. This includes supply & fixing of watering pipe & strip 65X5 mm brought out up to ground level. [ Earthong Should be tested for short circuit current rating of 40kA for 1 Sec. from approved laboratory. As per IS 3043. | Nos |  | 2 |  |  | 0 | 0
G.I Strip /Wire Earthing
Supply & laying of Hot Dipped G.I. (80 micron) earthing strip/wire.
E.1.18.1 | 75 x 10 mm GI Strip (For 33/11KV HT / Trafo Body) | Mtr. |  | Optional item. rate to be quoted
E.1.18.2 | 50 x 5 mm GI Strip (For Tapping, HT / Trafo Body) | Mtr. |  | 100
E.1.18.3 | 40 x 5mm GI Strip (For Tapping on Panel/ Equipment ) | Mtr. |  | Optional item. rate to be quoted
E.1.18.4 | 25 x 3mm GI Strip (For Tapping on Panel/ Equipment ) | Mtr. |  | 75
E.1.18.5 | 8 SWG Bare GI Wire | Mtr. |  | Optional item. rate to be quoted
E.1.18.6 | 10 SWG Bare GI. Wire | Mtr. |  | Optional item. rate to be quoted
Supply & Laying of EC GRADE 'CU' Strip /Earthing Wire. Including fixing at equipment end (with Insulators & other required hard wares)
E.1.18.8 | 40 x 5 mm Cu Strip | Mtr. |  | Optional item. rate to be quoted
E.1.18.9 | 25 x 3mm Cu Strip (For Tapping of Neutral/Static/Electronic Earthing) | Mtr. |  | 50
E.1.19 | 33 KV Copper XLPE cable 3CX300 sqmm | Mtrs. |  | 50 |  |  | 0 | 0
E.1.21 | Termination of 33 KV Copper XLPE cable 3CX300 sqmm Outdoor Type | Set |  | 2 |  |  | 0 | 0
E.1.23 | Termination of 33 KV Copper XLPE cable 3CX300 sqmm Indoor type | Set |  | 1 |  |  | 0 | 0
E.1.24 | Termination of 33 KV Alluminum XLPE cable 3CX400 sqmm Indoor type | Set |  | Optional item. rate to be quoted
E.1.25 | stay set | Nos |  | 2 |  |  | 0 | 0
E.1.26 | Out door 33 KV AB Switch 400amp | nos |  | 1 |  |  | 0 | 0
E.1.27 | 33 KV Drop out fuse(DO) 400 amps Sets complete with insulators & hard ware | nos |  | 3 |  |  | 0 | 0
E.1.28 | Lighting arrester 29 KV, | set |  | 1 |  |  | 0 | 0
E.1.29 | GI strip size 50X5 | Mtrs |  | 150 |  |  | 0 | 0
E.1.30 | 32X5 mm Copper Strip for LA earth | Mtrs |  | 75 |  |  | 0 | 0
E.1.31 | Concreting of H Beam and stay (20 mm / 25 mm) @ 0.3 cmt. per stay(apprx) | Cmt |  | 4.5 |  |  | 0 | 0
F | SAFETY EQUIPMENTS AND MISC ITEMS | [5 empty] | 0 | 0 | 0
F.1 | Supply & Fixing of Caution Boards. | No's |  | 2 |  |  | 0 | 0
F.2 | Supply & Fixing of Shock Treatment Chart in English & Hindi Language fixed on Ply & covered with 3mm thick plain glass. | No's |  | 2 |  |  | 0 | 0
F.3 | Supply of 33KV hand gloves duly tested. | Pair |  | 2 |  |  | 0 | 0
F.5 | Supply of 33KV DO Isolator Rod. | No. |  | 1 |  |  | 0 | 0
F.7 | Supply of Filled First Aid box complete with all standard medicines as per I.E rules. | No. |  | 2 |  |  | 0 | 0
F.8 | Sand bucket stand with 5 nos. MS. Buckets. | Set |  | 2 |  |  | 0 | 0
G | SUPPLY AND INSTALLATION OF FENCING & CIVIL MATERIAL. | [5 empty] | 0 | 0
G.1 | Supply & Installation of Fencing angle MS 65X65X5 (up to height 3 mtr) | Kg |  | 150 |  |  | 0 | 0
G. 2 | Supply & Installation of Fencing chain link of GI wire 10SWG 2.5Meter height | Sq Mtr |  | 75
G.2 | Supply & Installation of MS Gate with fabrication with two coats of epoxy primer and two coats of finsihed epoxy paint | kg |  | 100 |  |  | 0 | 0
G.3 | Supply & install Of earth chamber. Civil Work only | nos. |  | 6 |  |  | 0 | 0
G.4 | Supply & spreading of Gitti/Metal 40mm thik on yard and levelling of yard. | Cu.mtr |  | 4 |  |  | 0 | 0
| SECTION TOTAL- A | [5 empty] | 0 | 0 | 0
0
Total Basic Cost in figure
Total Basic Cost in words
E | Packing / forwarding freight and unloading at site
F | Transit insurance
G | GST
Total deliverable cost at KAPL site Ujjain
H | Extra if any
I | Are prices quoted firm till equipment delivery / Commissioning at KAPL Ujjain SITE | Y/N
2 | Bid validity date
3 | Guaranteed delivery date on EX KAPL Ujjain site basis
4 | Terms of payment
4.1 | For Indigenous Item
10% advance against advance bank guarantee valid till completion of project
50 % after delivery of material at site
30 % against installation
10% after commissioning and successful handing over to KAPL
All necessary statutory deductions like GST TDS, Income Tax TDS etc. shall be applicable as per Government norms
5 | Guarantees
6.1 | For satisfactory workman ship and against defective materials
6.2 | For Satisfactory performance
7 | Bank Guarantee
7.1 | For advance payment | Required
7.2 | For performance security(Security deposit) and performance gurantee | Required
8 | Delivery Period | 6 months from the Date of Letter of intent
9 | Insurance
9.1 | Contractor all risk policies(CAR) | Required
9.2 | Erection all risk policies(EAR ) | Required
NOTE :
Cost to be put in words and figure
Above quantity are estimated and it will be paid as per actual measurement after approval of DCPL/ KAPL
Material to be delivered at site after taking prior approval of techanical and quantity from DCPL/KAPL
Each material which is supplied at required OEM test cetificate with out that Invoice will not consider